## INTRODUCTION
INTRODUCTION
Welcome to the simulation exercise work sheet of HyCool project. This file is necessary to solve exercise latent heat storage. Use the boxes yellow marked boxes to fill your result. You don't need to fill any units, units are already default. If the answer is correct, the box will turn green. If it is wrong, the box will turn red.
Emtpy field
Correct answer | 5
wrong answer | 6

## Exercise Latent heat storage
System simulation exercise: latent heat storage
This Excel file helps to solve the online test. The exercise focuses on a comparison between sensible and latent heat storage systems. Furthermore, the impact of different storage materials will be investigated.
● | Calculate the mass and volume-specific heat storage capacity for the given temperature band for the heat storage medium water and PCM. For these calculations, please consider the used units.
● | Sketch the curve of the mass-specific heat storage capacity of water and PCM over the specified temperature range. For this, you need to fill the table with data for both water and PCM. Fill the table with amount of energy stored for each temperature step. The table starts with 0 kJ/kg at 50°C.
● | In a exemplary system, a storage tank with a capacity of 200 kWh is required. Calculate the corresponding volume for both the sensible heat storage (water) and the latent heat storage (using PCM).
Boundaries
System:
| load temperature |  |  | 50
| discharge temperature |  |  | 80
Material properties
| spec. heat capacity water |  |  | 4.19
| density water |  |  | 1000
| spec. heat capacity PCM (fluid) |  |  | 1.8
| spec. heat capacity PCM (solid) |  |  | 1.5
| phase change enthalpy PCM |  |  | 120
| phase change temperature |  |  | 65
| density PCM (simplified for solid & fluid) |  |  | 850
Equations
Sensible heat storage
Sensible heat storage + latent heat
Mass-/ volume-specific heat capacities
mass-specific heat capacity water
volume-specific heat capacity water
mass-specific heat capacity PCM
volume-specific heat capacity PCM
Data table for figure on the right
| temperature | water | PCM
| 50 | 0 | 0
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
Solution storage volume
Conversion storage heat capacity into kJ
Storage volume using water
Storage volume using PCM
𝑄= 𝑐_𝑝 ∗𝑚 ∗ Δ𝑇
1 𝑘𝑊ℎ=3600 𝑘𝐽
𝑄= 𝑐_𝑝 ∗𝑚 ∗ Δ𝑇_1+ℎ_𝑃𝐶+ 𝑐_𝑝 ∗𝑚 ∗ Δ𝑇_2

## Exercise storage - Solution (hidden)
Execise 1
● | Calculate the mass and volume-specific heat storage capacity for the given temperature band for the heat storage medium water and PCM.
● | Sketch the curve of the mass-specific heat storage capacity of water and PCM over the specified temperature range.
● | In a system a storage tank with a capacity of 200 kWh is required. Calculate the corresponding volume for both the sensitive and the latent heat storage.
Boundaries
System:
| load temperature |  |  | 50
| discharge temperature |  |  | 80
Material properties
| spec. heat capacity water |  |  | 4.19
| density water |  |  | 1000
| spec. heat capacity PCM (fluid) |  |  | 1.8
| spec. heat capacity PCM (solid) |  |  | 1.5
| phase change enthalpy PCM |  |  | 120
| phase change temperature |  |  | 65
| density PCM |  |  | 850
Equations
Sensible heat storage
Sensible heat storage + latent heat
Solution
● | mass-specific heat capacity water |  |  |  | 125.7
| colume-specific heat capacity water |  |  |  | 125700
| mass-specific heat capacity PCM |  |  |  | 169.5
| volume-specific heat capacity PCM |  |  |  | 144075
● | temperature | water | PCM
| 50 | 0 | 0
| 51 | 4.19 | 1.5
| 52 | 8.38 | 3
| 53 | 12.57 | 4.5
| 54 | 16.76 | 6
| 55 | 20.95 | 7.5
| 56 | 25.14 | 9
| 57 | 29.33 | 10.5
| 58 | 33.52 | 12
| 59 | 37.71 | 13.5
| 60 | 41.9 | 15
| 61 | 46.09 | 16.5
| 62 | 50.28 | 18
| 63 | 54.47 | 19.5
| 64 | 58.66 | 21
| 65 | 62.85 | 142.5
| 66 | 67.04 | 144.3
| 67 | 71.23 | 146.1
| 68 | 75.42 | 147.9
| 69 | 79.61 | 149.7
| 70 | 83.8 | 151.5
| 71 | 87.99 | 153.3
| 72 | 92.18 | 155.1
| 73 | 96.37 | 156.9
| 74 | 100.56 | 158.7
| 75 | 104.75 | 160.5
| 76 | 108.94 | 162.3
| 77 | 113.13 | 164.1
| 78 | 117.32 | 165.9
| 79 | 121.51 | 167.7
| 80 | 125.7 | 169.5
● | Conversion heat capacity into kJ |  |  |  | 720000
| Calculation storage volume water |  |  |  | 5.7279
| Calculation storage volume PCM |  |  |  | 4.9974
𝑄^′=4.19 𝑘𝐽/𝑘𝑔𝐾∗ (65 −50)𝐾 +120 𝑘𝐽/𝑘𝑔+1.80 𝑘𝐽/𝑘𝑔𝐾 ∗(80 −65)𝐾=169.5 𝑘𝐽/𝑘𝑔
𝑄^′=125.7 𝑘𝐽/𝑘𝑔 ∗1,000 𝑘𝑔/𝑚^3 =125,700 𝑘𝐽/𝑚³
𝑄^′=4.19 𝑘𝐽/𝑘𝑔𝐾∗ (80 −50)𝐾=125.7 𝑘𝐽/𝑘𝑔
𝑄^′=169.5 𝑘𝐽/𝑘𝑔 ∗800 𝑘𝑔/𝑚^3 =144,075 𝑘𝐽/𝑚³
𝑄= 𝑐_𝑝 ∗𝑚 ∗ Δ𝑇
1 𝑘𝑊ℎ=3600 𝑘𝐽
200 𝑘𝑊ℎ=720,000 𝑘𝐽
𝑉=(720,000 𝑘𝐽)/(125,700 𝑘𝐽/𝑚³)=5.73 𝑚³
𝑉=(720,000 𝑘𝐽)/(144,075 𝑘𝐽/𝑚³)=5.00 𝑚³
𝑄= 𝑐_𝑝 ∗𝑚 ∗ Δ𝑇_1+ℎ_𝑃𝐶+ 𝑐_𝑝 ∗𝑚 ∗ Δ𝑇_2