## INTRODUCTION
INTRODUCTION
Welcome to the simulation exercise work sheet of HyCool project. This file is necessary to solve exercise solar cooling, part A. Use the boxes yellow marked boxes to fill your result. You don't need to fill any units, units are already default. If the answer is correct, the box will turn green. If it is wrong, the box will turn red.
Emtpy field
Correct answer | 5
wrong answer | 6

## exercise solar cooling, part A
Exercise solar cooling, part A
This exercise covers a solar thermal cooling applicaiton in combination with industrial heat processes. A plant fo concentrating solar collector generates ehat to supply primarily an adsorption chiller and secondary process heat applications.
● | Calculate the heat output per hour generated by the collector field. Use the table below.
● | The chiller can take a maximum heat output of 200 kW, excess heat is used for other processes. Calculate the cooling capacity of the chiller with the given COP and the heat available for other processes.
● | To what percentage does thermal cooling cover the cooling demand on a given day?
Boundaries
| Collector plant size |  |  |  |  | 1200
| min. direct radiation as indicator of system process |  |  |  |  | 100
| collector efficiency (simplified) |  |  |  |  | 0.45
| max. heat consumption chiller |  |  |  |  | 200
| COP chiller |  |  |  |  | 0.4
| cooling demand |  |  |  |  | 100
solar radiation
| Time | Total | direct | Qheat | Qchil | QProcess | Qchill_demand
| [hour] | [W/m²] | [W/m²] | [kWh] | [kWh] | [kWh] | [kWh]
| 0:00 | 0 | 0 |  |  |  | 0
| 1:00 | 0 | 0 |  |  |  | 0
| 2:00 | 0 | 0 |  |  |  | 0
| 3:00 | 0 | 0 |  |  |  | 0
| 4:00 | 0 | 0 |  |  |  | 0
| 5:00 | 50 | 30 |  |  |  | 0
| 6:00 | 100 | 60 |  |  |  | 0
| 7:00 | 150 | 90 |  |  |  | 100
| 8:00 | 250 | 150 |  |  |  | 100
| 9:00 | 400 | 240 |  |  |  | 100
| 10:00 | 600 | 360 |  |  |  | 100
| 11:00 | 800 | 480 |  |  |  | 100
| 12:00 | 1000 | 600 |  |  |  | 100
| 13:00 | 950 | 570 |  |  |  | 100
| 14:00 | 900 | 540 |  |  |  | 100
| 15:00 | 800 | 480 |  |  |  | 100
| 16:00 | 700 | 420 |  |  |  | 100
| 17:00 | 500 | 300 |  |  |  | 100
| 18:00 | 300 | 180 |  |  |  | 100
| 19:00 | 150 | 90 |  |  |  | 0
| 20:00 | 100 | 60 |  |  |  | 0
| 21:00 | 50 | 30 |  |  |  | 0
| 22:00 | 0 | 0 |  |  |  | 0
| 23:00 | 0 | 0 |  |  |  | 0
Equations
●
●
Solution
solar radiation
|  | Total | direct | Qheat | Qchil | QProcess | Qchill_demand
|  | [W/m²] | [W/m²] | [kWh] | [kWh] | [kWh] | [kWh]
| 0:00 | 0 | 0 |  |  |  | 0
| 1:00 | 0 | 0 |  |  |  | 0
| 2:00 | 0 | 0 |  |  |  | 0
| 3:00 | 0 | 0 |  |  |  | 0
| 4:00 | 0 | 0 |  |  |  | 0
| 5:00 | 50 | 30 |  |  |  | 0
| 6:00 | 100 | 60 |  |  |  | 0
| 7:00 | 150 | 90 |  |  |  | 80
| 8:00 | 250 | 150 |  |  |  | 80
| 9:00 | 400 | 240 |  |  |  | 80
| 10:00 | 600 | 360 |  |  |  | 80
| 11:00 | 800 | 480 |  |  |  | 80
| 12:00 | 1000 | 600 |  |  |  | 80
| 13:00 | 950 | 570 |  |  |  | 80
| 14:00 | 900 | 540 |  |  |  | 80
| 15:00 | 800 | 480 |  |  |  | 80
| 16:00 | 700 | 420 |  |  |  | 80
| 17:00 | 500 | 300 |  |  |  | 80
| 18:00 | 300 | 180 |  |  |  | 80
| 19:00 | 150 | 90 |  |  |  | 0
| 20:00 | 100 | 60 |  |  |  | 0
| 21:00 | 50 | 30 |  |  |  | 0
| 22:00 | 0 | 0 |  |  |  | 0
| 23:00 | 0 | 0 |  |  |  | 0
| SUM | 7800 | 4680 | 0 | 0 | 0 | 960
𝑄_ℎ𝑒𝑎𝑡= η_𝑐𝑜𝑙𝑙 ∗ 𝐸_𝑑𝑖𝑟𝑒𝑐𝑡^𝑠𝑜𝑙𝑎𝑟 ∗𝐴_𝑐𝑜𝑙𝑙
𝑄_𝑐ℎ𝑖𝑙𝑙= 𝑄_ℎ𝑒𝑎𝑡 ∗𝐶𝑂𝑃
𝑄_𝑃𝑟𝑜𝑐𝑒𝑠𝑠=𝑀𝑎𝑥(0; 𝑄_ℎ𝑒𝑎𝑡 −200)
Please watch the unit: 1000 W = 1 kW

## Exercise part A - Solution (hidden)
Exercise 2.1
a) | Calculate the heat output per hour generated by the collector field.
b) | The chiller can take a maximum heat output of 200 kW, excess heat is used for other processes. Calculate the cooling capacity of the chiller with the given COP and the heat available for other processes.
c) | To what percentage does thermal cooling cover the cooling demand on a given day?
Boundaries
| Collector plant size |  |  |  |  | 1200
| min. direct radiation as indicator of system process |  |  |  |  | 100
| collector efficiency (simplified) |  |  |  |  | 0.45
| max. heat consumption chiller |  |  |  |  | 200
| COP chiller |  |  |  |  | 0.4
| cooling demand |  |  |  |  | 100
solar radiation
| Time | Total | direct | Qheat | Qchil | QProcess | Qchill_demand
| [hour] | [W/m²] | [W/m²] | [kWh] | [kWh] | [kWh] | [kWh]
| 0:00 | 0 | 0 | 0 | 0 | 0 | 0
| 1:00 | 0 | 0 | 0 | 0 | 0 | 0
| 2:00 | 0 | 0 | 0 | 0 | 0 | 0
| 3:00 | 0 | 0 | 0 | 0 | 0 | 0
| 4:00 | 0 | 0 | 0 | 0 | 0 | 0
| 5:00 | 50 | 30 | 0 | 0 | 0 | 0
| 6:00 | 100 | 60 | 0 | 0 | 0 | 0
| 7:00 | 150 | 90 | 0 | 0 | 0 | 100
| 8:00 | 250 | 150 | 81 | 32.4 | 0 | 100
| 9:00 | 400 | 240 | 129.6 | 51.84 | 0 | 100
| 10:00 | 600 | 360 | 194.4 | 77.76 | 0 | 100
| 11:00 | 800 | 480 | 259.2 | 80 | 59.2 | 100
| 12:00 | 1000 | 600 | 324 | 80 | 124 | 100
| 13:00 | 950 | 570 | 307.8 | 80 | 107.8 | 100
| 14:00 | 900 | 540 | 291.6 | 80 | 91.6 | 100
| 15:00 | 800 | 480 | 259.2 | 80 | 59.2 | 100
| 16:00 | 700 | 420 | 226.8 | 80 | 26.8 | 100
| 17:00 | 500 | 300 | 162 | 64.8 | 0 | 100
| 18:00 | 300 | 180 | 97.2 | 38.88 | 0 | 100
| 19:00 | 150 | 90 | 0 | 0 | 0 | 0
| 20:00 | 100 | 60 | 0 | 0 | 0 | 0
| 21:00 | 50 | 30 | 0 | 0 | 0 | 0
| 22:00 | 0 | 0 | 0 | 0 | 0 | 0
| 23:00 | 0 | 0 | 0 | 0 | 0 | 0
Equations
a)
b)
Solution a) & b)
|  | Total | direct | Qheat | Qchil | QProcess | Qchill_demand
|  | [W/m²] | [W/m²] | [kWh] | [kWh] | [kWh] | [kWh]
| 0:00 | 0 | 0 | 0 | 0 | 0 | 0
| 1:00 | 0 | 0 | 0 | 0 | 0 | 0
| 2:00 | 0 | 0 | 0 | 0 | 0 | 0
| 3:00 | 0 | 0 | 0 | 0 | 0 | 0
| 4:00 | 0 | 0 | 0 | 0 | 0 | 0
| 5:00 | 50 | 30 | 0 | 0 | 0 | 0
| 6:00 | 100 | 60 | 0 | 0 | 0 | 0
| 7:00 | 150 | 90 | 0 | 0 | 0 | 100
| 8:00 | 250 | 150 | 81 | 32.4 | 0 | 100
| 9:00 | 400 | 240 | 129.6 | 51.84 | 0 | 100
| 10:00 | 600 | 360 | 194.4 | 77.76 | 0 | 100
| 11:00 | 800 | 480 | 259.2 | 80 | 59.2 | 100
| 12:00 | 1000 | 600 | 324 | 80 | 124 | 100
| 13:00 | 950 | 570 | 307.8 | 80 | 107.8 | 100
| 14:00 | 900 | 540 | 291.6 | 80 | 91.6 | 100
| 15:00 | 800 | 480 | 259.2 | 80 | 59.2 | 100
| 16:00 | 700 | 420 | 226.8 | 80 | 26.8 | 100
| 17:00 | 500 | 300 | 162 | 64.8 | 0 | 100
| 18:00 | 300 | 180 | 97.2 | 38.88 | 0 | 100
| 19:00 | 150 | 90 | 0 | 0 | 0 | 0
| 20:00 | 100 | 60 | 0 | 0 | 0 | 0
| 21:00 | 50 | 30 | 0 | 0 | 0 | 0
| 22:00 | 0 | 0 | 0 | 0 | 0 | 0
| 23:00 | 0 | 0 | 0 | 0 | 0 | 0
| SUM | 7800 | 4680 | 2332.8 | 745.68 | 468.6 | 1200
Solution c)
[5 empty] | 62.14% | 62%
𝑄_ℎ𝑒𝑎𝑡= η_𝑐𝑜𝑙𝑙 ∗ 𝐸_𝑑𝑖𝑟𝑒𝑐𝑡^𝑠𝑜𝑙𝑎𝑟 ∗𝐴_𝑐𝑜𝑙𝑙
𝑄_𝑐ℎ𝑖𝑙𝑙= 𝑄_ℎ𝑒𝑎𝑡 ∗𝐶𝑂𝑃
𝑄_𝑃𝑟𝑜𝑐𝑒𝑠𝑠=𝑀𝑎𝑥(0; 𝑄_ℎ𝑒𝑎𝑡 −200)
𝑆𝑜𝑙𝑎𝑟 𝑟𝑎𝑡𝑖𝑜 = (745.7 𝑘𝑊ℎ)/(1200 𝑘𝑊ℎ)= 62 %