## INTRODUCTION
INTRODUCTION
Welcome to the simulation exercise work sheet of HyCool project. This file is necessary to solve exercise solar cooling, part B. Use the boxes yellow marked boxes to fill your result. You don't need to fill any units, units are already default. If the answer is correct, the box will turn green. If it is wrong, the box will turn red.
Emtpy field
Correct answer | 5
wrong answer | 6

## exercise solar cooling, part B
Exercise solar cooling, part B
We are looking at the same plant as in the exercise solar cooling, part A. Now, however, the excess solar heat is not used for processes, but is stored for later use in the chiller.
● | Calculate the heat generated by the solar collector plant, the chilling capacity and the stored heat in the tank for the day under consideration. Consider that heat from storage can be used for supply of the chiller, if the solar power is low.
● | What amount of energy is stored in the energy storage at the end of the day?
● | What is the total requried maximum capacity of the storage?
Boundaries
The chiller is running only, when there is cooling demand at the same time.
The heat storage is fully discharged in the beginning of the day.
| Collector plant size |  |  |  |  | 1200
| min. direct radiation as indicator of system process |  |  |  |  | 100
| collector efficiency (simplified) |  |  |  |  | 0.45
| max. heat consumption chiller |  |  |  |  | 200
| COP chiller |  |  |  |  | 0.4
| cooling demand |  |  |  |  | 100
solar radiation
| Time | Total | direct | Qheat | Qchil | Qstorage | Qchill_demand
| [hour] | [W/m²] | [W/m²] | [kWh] | [kWh] | [kWh] | [kWh]
| 0:00 | 0 | 0 |  |  |  | 0
| 1:00 | 0 | 0 |  |  |  | 0
| 2:00 | 0 | 0 |  |  |  | 0
| 3:00 | 0 | 0 |  |  |  | 0
| 4:00 | 0 | 0 |  |  |  | 0
| 5:00 | 50 | 30 |  |  |  | 0
| 6:00 | 100 | 60 |  |  |  | 0
| 7:00 | 150 | 90 |  |  |  | 100
| 8:00 | 250 | 150 |  |  |  | 100
| 9:00 | 400 | 240 |  |  |  | 100
| 10:00 | 600 | 360 |  |  |  | 100
| 11:00 | 800 | 480 |  |  |  | 100
| 12:00 | 1000 | 600 |  |  |  | 100
| 13:00 | 950 | 570 |  |  |  | 100
| 14:00 | 900 | 540 |  |  |  | 100
| 15:00 | 800 | 480 |  |  |  | 100
| 16:00 | 700 | 420 |  |  |  | 100
| 17:00 | 500 | 300 |  |  |  | 100
| 18:00 | 300 | 180 |  |  |  | 100
| 19:00 | 200 | 120 |  |  |  | 0
| 20:00 | 100 | 60 |  |  |  | 0
| 21:00 | 50 | 30 |  |  |  | 0
| 22:00 | 0 | 0 |  |  |  | 0
| 23:00 | 0 | 0 |  |  |  | 0
Equations
●
●
Solution
solar radiation
| Time | Total | direct | Qheat | Qchil | Qstorage | Qchill_demand
| [hour] | [W/m²] | [W/m²] | [kWh] | [kWh] | [kWh] | [kWh]
| 0:00 | 0 | 0 |  |  |  | 0
| 1:00 | 0 | 0 |  |  |  | 0
| 2:00 | 0 | 0 |  |  |  | 0
| 3:00 | 0 | 0 |  |  |  | 0
| 4:00 | 0 | 0 |  |  |  | 0
| 5:00 | 50 | 30 |  |  |  | 0
| 6:00 | 100 | 60 |  |  |  | 0
| 7:00 | 150 | 90 |  |  |  | 80
| 8:00 | 250 | 150 |  |  |  | 80
| 9:00 | 400 | 240 |  |  |  | 80
| 10:00 | 600 | 360 |  |  |  | 80
| 11:00 | 800 | 480 |  |  |  | 80
| 12:00 | 1000 | 600 |  |  |  | 80
| 13:00 | 950 | 570 |  |  |  | 80
| 14:00 | 900 | 540 |  |  |  | 80
| 15:00 | 800 | 480 |  |  |  | 80
| 16:00 | 700 | 420 |  |  |  | 80
| 17:00 | 500 | 300 |  |  |  | 80
| 18:00 | 300 | 180 |  |  |  | 80
| 19:00 | 150 | 90 |  |  |  | 0
| 20:00 | 100 | 60 |  |  |  | 0
| 21:00 | 50 | 30 |  |  |  | 0
| 22:00 | 0 | 0 |  |  |  | 0
| 23:00 | 0 | 0 |  |  |  | 0
| SUM | 7800 | 4680 | 0 | 0 |  | 960
Energy stored in the tank at the end of the day:
Maximum capacity of the storage during the day:
𝑄_ℎ𝑒𝑎𝑡= η_𝑐𝑜𝑙𝑙 ∗ 𝐸_𝑑𝑖𝑟𝑒𝑐𝑡^𝑠𝑜𝑙𝑎𝑟 ∗𝐴_𝑐𝑜𝑙𝑙
𝑄_𝑐ℎ𝑖𝑙𝑙= 𝑄_ℎ𝑒𝑎𝑡 ∗𝐶𝑂𝑃
Please watch the unit: 1000 W = 1 kW

## Exercise part B - Solution (hidden)
Exercise 2.2
a) | We are looking at the same plant as before. Now, however, the excess solar heat is not used for processes, but is stored for later use in the chiller. Calculate the stored heat in the tank for the day under consideration.
b) | Determine from the data the amount of energy that the memory should absorb for the day in question. Heat losses are not considered.
Boundaries
The chiller is running only, when there is cooling demand at the same time.
The heat storage is fully discharged in the beginning of the day.
| Collector plant size |  |  |  |  | 1200
| min. direct radiation as indicator of system process |  |  |  |  | 100
| collector efficiency (simplified) |  |  |  |  | 0.45
| max. heat consumption chiller |  |  |  |  | 200
| COP chiller |  |  |  |  | 0.4
| cooling demand |  |  |  |  | 100
solar radiation
| Time | Total | direct | Qheat | Qchil | Qstorage | Qchill_demand
| [hour] | [W/m²] | [W/m²] | [kWh] | [kWh] | [kWh] | [kWh]
| 0:00 | 0 | 0 |  |  |  | 0
| 1:00 | 0 | 0 |  |  |  | 0
| 2:00 | 0 | 0 |  |  |  | 0
| 3:00 | 0 | 0 |  |  |  | 0
| 4:00 | 0 | 0 |  |  |  | 0
| 5:00 | 50 | 30 |  |  |  | 0
| 6:00 | 100 | 60 |  |  |  | 0
| 7:00 | 150 | 90 |  |  |  | 100
| 8:00 | 250 | 150 |  |  |  | 100
| 9:00 | 400 | 240 |  |  |  | 100
| 10:00 | 600 | 360 |  |  |  | 100
| 11:00 | 800 | 480 |  |  |  | 100
| 12:00 | 1000 | 600 |  |  |  | 100
| 13:00 | 950 | 570 |  |  |  | 100
| 14:00 | 900 | 540 |  |  |  | 100
| 15:00 | 800 | 480 |  |  |  | 100
| 16:00 | 700 | 420 |  |  |  | 100
| 17:00 | 500 | 300 |  |  |  | 100
| 18:00 | 300 | 180 |  |  |  | 100
| 19:00 | 200 | 120 |  |  |  | 0
| 20:00 | 100 | 60 |  |  |  | 0
| 21:00 | 50 | 30 |  |  |  | 0
| 22:00 | 0 | 0 |  |  |  | 0
| 23:00 | 0 | 0 |  |  |  | 0
Equations
Solution a)
| Time | Total | direct | Qheat | Qchil | Qstorage | Qchill_demand
| [hour] | [W/m²] | [W/m²] | [kWh] | [kWh] | [kWh] | [kWh]
| 0:00 | 0 | 0 | 0 | 0 | 0 | 0
| 1:00 | 0 | 0 | 0 | 0 | 0 | 0
| 2:00 | 0 | 0 | 0 | 0 | 0 | 0
| 3:00 | 0 | 0 | 0 | 0 | 0 | 0
| 4:00 | 0 | 0 | 0 | 0 | 0 | 0
| 5:00 | 50 | 30 | 0 | 0 | 0 | 0
| 6:00 | 100 | 60 | 0 | 0 | 0 | 0
| 7:00 | 150 | 90 | 0 | 0 | 0 | 100
| 8:00 | 250 | 150 | 81 | 32.4 | 0 | 100
| 9:00 | 400 | 240 | 129.6 | 51.84 | 0 | 100
| 10:00 | 600 | 360 | 194.4 | 77.76 | 0 | 100
| 11:00 | 800 | 480 | 259.2 | 80 | 59.2 | 100
| 12:00 | 1000 | 600 | 324 | 80 | 183.2 | 100
| 13:00 | 950 | 570 | 307.8 | 80 | 291 | 100
| 14:00 | 900 | 540 | 291.6 | 80 | 382.6 | 100
| 15:00 | 800 | 480 | 259.2 | 80 | 441.8 | 100
| 16:00 | 700 | 420 | 226.8 | 80 | 468.6 | 100
| 17:00 | 500 | 300 | 162 | 80 | 430.6 | 100
| 18:00 | 300 | 180 | 97.2 | 80 | 327.8 | 100
| 19:00 | 150 | 90 | 0 | 0 | 327.8 | 0
| 20:00 | 100 | 60 | 0 | 0 | 327.8 | 0
| 21:00 | 50 | 30 | 0 | 0 | 327.8 | 0
| 22:00 | 0 | 0 | 0 | 0 | 327.8 | 0
| 23:00 | 0 | 0 | 0 | 0 | 327.8 | 0
| Sum: | 7800 | 4680 | 2332.8 | 802 | 468.6 | 1200
Solution b)
327.8
Solution c)
468.6
𝑄_ℎ𝑒𝑎𝑡= η_𝑐𝑜𝑙𝑙 ∗ 𝐸_𝑑𝑖𝑟𝑒𝑐𝑡^𝑠𝑜𝑙𝑎𝑟 ∗𝐴_𝑐𝑜𝑙𝑙
𝑄_𝑐ℎ𝑖𝑙𝑙= 𝑄_ℎ𝑒𝑎𝑡 ∗𝐶𝑂𝑃
𝑄_𝑠𝑡𝑜𝑟𝑎𝑔𝑒=max⁡(𝑄_𝑠𝑡𝑜𝑟𝑎𝑔𝑒 )=468.6 𝑘𝑊ℎ